## Fire
Date
22-Jan-2018 |  | FIRE SAFETY
Bangladesh Accord Remediation Summary of Actions Required
Factory Name & Address |  | Sawftex Ltd, Bhangnahati, Sreepur, Gazipur, Dhaka
Date of Inspection by Accord |  | 2014-02-17
Accord Rating
Finance Plan Agreed |  | Yes
Item No | Accord Inspection Observation | Accord Action Plan | Final Action Plan | Final Timeline | Comments from Accord | Accord Timeline | Progress Status
1 | Fire doors are in the process of being installed. | Provide listed outward swinging, fire-rated doors at all openings into stairs and at hazard separation areas. |  | 20/11/2015 | On 29/05/16: Corrected. Note: If factory wants to keep the door open than factory shall be installed magnetic door holder. If factory uses room for any propose under exit stair, they shall be separated it with fire rated construction. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. | 12/31/2014 | Corrected
2 | . | Install a Class III standpipe system at required locations. If full automatic sprinkler protection is provided, only a Class I system is needed. Standpipe system must comply with NFPA 14. |  | 30/11/2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Issue reopened. | 12/31/2014 | Corrected
3 | There were unprotected penetrations through the floor at each electrical cabinet location. Additionally, the fire sprinkler risers need to be protected at the floor openings. | Provide fire-resistive rated opening or penetration protection for rated walls and assemblies in accordance with Alliance Standard Sections 4.6 and 4.7. Consult a qualified fire protection engineer to design the required opening protectives or penetration systems. |  | 30/06/2015 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. | 12/31/2014 | Corrected
4 | Automatic protection systems being installed. | Install a dedicated fire pump for the facility in accordance with NFPA 20. Also, install a water storage tank in accordance with NFPA 22. Submit plans of under construction system to Alliance for review. |  | 30/11/2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Issue reopened. | 12/31/2014 | Corrected
5 | Fire alarm panel does not report to a central facility. Additionally, the fire pump is not monitored by the fire alarm panel. | Arrange for direct connection of the fire alarm and detection system to a central station monitoring service or the Fire Service and Civil Defence per Alliance Standard Part 5 Section 5.7.5 Monitoring. Until that time that a central station monitoring service or direct connection to the Fire Service and Civil Defence can be set up, a person trained to contact the Fire Service and Civil Defence in the event of fire alarm activation shall be provided. An annunciator shall be located in a constantly attended location (such as a fire control room) to alert this person. Have the fire pump conditions monitored by the fire alarm panel in accordance with NFPA 20. |  | 30/06/2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Issue reopened. | 12/31/2014 | Corrected
6 | Battery exit lighting is provided | Install emergency lighting for all paths of egress in accordance with Alliance Standard Section 6.7. |  | 30/06/2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. | 12/31/2014 | Corrected
7 | Handrails are provided on one side of the stair only. | Provide handrails on both sides of each stairway. Mount handrails at a height between 30 in. and 44 in. |  | 29/05/2016 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. | 12/31/2014 | Corrected
8 | Exit signs are provided at the stairs. | Provide continuously illuminated exit signs per Alliance Standard Section 6.11. Signs shall be placed at all required exits and along egress paths, especially where there is a change in direction for the path of travel. |  | 12/05/2015 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. | 12/31/2014 | Corrected
9 | Occupant load signage is not provided. | Post the occupant load for all assembly and production floor areas in a conspicuous space near the main exit or exit access doorway for the space. |  | 12/05/2015 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. | 12/31/2014 | Corrected
10 | No certificate of occupancy provided for review. | Obtain the the Certificates of Occupancy for each building and ancillary structure according to building use from the approving authority. |  | 12/05/2015 | On 29/05/16: Not applicable. On 01/09/16: Not applicable. On 13/08/17: Not applicable. On 20/11/2017: Corrected. N/A. | 12/31/2014 | Corrected
11 | The egress path along means of egress has interrupted by obstruction/storage. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. |  | 09/06/2016 | On 29/05/16: New Finding. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. | Immediately | Corrected
12 | New Finding (4th FU): Heavy fire load has been observed at the production floors due to the presence of large area of unenclosed combustible storages. | Provide defined storage areas and limit the storage arrangement as Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress
13 | New Finding (4th FU): Staff dinning at ground floor was observed inside the store room. | Remove dinning from the location Or Provide 3-hr fire separation with direct exit discharge. |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress
14 | New Finding (4th FU): The exit discharge path from store and other areas at ground floor is less than 10 ft. wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress
15 | New Finding (4th FU): Storage was located in the exit stair enclosure. | Remove all storage from exit stairs. |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress
16 | New Finding (4th FU): Proper third party certification for fire pump was not available. | Provide proper third party certification for fire pump. |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress
17 | New Finding (4th FU): During inspection it was observed that the auto-start for the fire pumps were non-functional. | Install fire pump as per NFPA-20 |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress
18 | New Finding (4th FU): Installed stand-pipe system were not as per NFPA-14. | Provide standpipe and hose system as per NFPA 14 & 20. |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress
19 | New Finding (4th FU): Installed Fire alarm system were observed not as per NFPA-72. Battery were undersized, No supervision for Sounders were observed. | Modify the current addressable fire alarm system in accordance with NFPA 72. |  | 21/12/2017 | On 20/11/2017: New Finding | Within 1 month | In Progress