## Structural
Date
22-Jan-2018 |  | STRUCTURAL & BUILDING SAFETY
Bangladesh Accord Remediation Summary of Actions Required
Factory Name & Address |  | Sawftex Ltd, Bhangnahati, Sreepur, Gazipur, Dhaka
Date of Inspection by Accord |  | 2014-03-07
Accord Rating
Finance Plan Agreed |  | Yes
Item No | Accord Inspection Observation | Accord Action Plan | Final Action Plan | Final Timeline | Comments from Accord | Accord Timeline | Progress Status
1 | An expansion at the NW corner of the building for worker latrines was observed during our walk through, and a new fire egress stair was observed at the SW corner of the building. Documentation for these structures were not available for review at the time of our visit. | Have a qualified structural engineer complete an analytical evaluation of the structural impact of the addition. Provide record drawings for these expansions by the engineer of record. A detailed assessment of cantilevered slabs at the NW expansion is required. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
2 | We did not observe special provisions for concentrated loads in the structure. We observed 2000L and 3000L water tanks at the roof top level. | Engage a qualified structural engineer to confirm and document that provisions have been made to accommodate concentrated loads. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Corrected by ALLIANCE | 30/06/2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. Factory have shifted plastic water tank to another location . | 1/31/2015 | Corrected
3 | Wind and seismic design information not provided on available record documents. | Have a qualified structural engineer document compliance with the seismic and wind requirements stated in the 2006 BNBC. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
4 | Design criteria was not included on available record documents. | Engage a qualified structural engineer to confirm satisfactory structural performance of the buildings under wind loading. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
5 | Rooftop cable-stayed antenna and water tanks are not braced for seismic forces. Cable anchors for the antenna were noted to be of poor construction. | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
6 | No program was in place at the time of our visit. | Develop a program to ensure that all live loads for which a floor or roof has been designed for will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
7 | General notes are missing from the structural documents. The design code for the building is not indicated on structural documents. Material strengths used for the design are not indicated on the structural documents. | Provide general notes with design criteria and material strengths from the Engineer of Record. Engage a qualified structural engineer to develop the required documents to confirm the structural integrity of the buildings. Documents must comply with Alliance Standard Part 8 Section 8.19 and 8.20 | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
8 | Exposed reinforcing bars at the NW expansion and roof should be removed and protected from future corrosion. Visible water was noted to be present on the roof that is leaking from rooftop plumbing. | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up inspection no water ponding found on the roof. | 1/31/2015 | Corrected
9 | As part of the follow up work by EIMS (detailed elsewhere via the column FoS question) conducted following the site visit by Walter P Moore, it was determined that MCAC was used in the construction of the building, including the roof slab. No protective coating was provided at the roof level of the building. | Provide a protective coating at the structural elements constructed with MCAC exposed to rainfall or other sources of water. Have protective coating approved by the Alliance or a qualified structural engineer. | Corrected by ALLIANCE | 30/06/2015 | On 24/10/2016: During follow up visit it was found protective coating has been provided. | 1/31/2015 | Corrected
10 | Certificates of Occupancy were not available at the time of our visit. | Provide Certificates of Occupancy for review. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: As per alliance report,it has been corrected. | 1/31/2015 | Corrected
11 | A designated load manager was not present or on staff at the time of our visit. | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to RMG vendors and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: Found corrected by ALLIANCE. | 1/31/2015 | Corrected
12 | Load Plans were not available at the time of our visit. | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3 | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found that load plan for each floor was prepared and loading at all floors were found as per as built load plan. Design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
13 | Posted load plans were not observed at the time of our visit. | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: During follow up visit it was found that load plan for each floor was prepared and posted and loading at all floors were found as per as built load plan. Design report has been approved by Alliance on 03 November 2015. | 1/31/2015 | Corrected
14 | Load limits in storage areas were not clearly marked. | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Corrected by ALLIANCE | 12/05/2015 | On 24/10/2016: As per alliance report,it has been corrected. | 1/31/2015 | Corrected
15 | Joint between NW expansion and main building is cracking. No expansion joint was provided and the slab at each of these levels has cracked. | Install joint between original building and NW expansion. Remove deteriorated expansion joint material and provide new approved material at the expansion joint. | Corrected by ALLIANCE | 30/06/2015 | On 24/10/2016: During follow up visit it was found expansion joint has been covered by metal . | 1/31/2015 | Corrected